**ROV**an**CO**

20535 S.E. FRONTAGE ROAD

JOLIET, ILLINOIS 60431

PHONE: 815-741-6700

FAX: 815-741-9080

Email: chad@rovanco.com

Website: [www.rovanco.com](http://www.rovanco.com)

***Piping Systems, Inc*.**

November 13, 2023

**Part 1 – General**

**1.01 Above Ground Pre-Insulated Foam System with Fusio-technik® PP-RCT125 Carrier Pipe**

**1.02 This piping system** shall be **Fusio-technik®** **PP-RCT125 WOR carrier pipe x spiral lock seam metal jacket pre-insulated with HiTherm PIR300 25/50 polyisocyanurate foam** as manufactured by **Rovanco® Piping Systems** of Joliet, Illinois.

**Part 2 - Products**

**2.01 Carrier Pipe** Pipe shall be manufactured by Aquatechnik® Polypropylene Random   
Co-Polymer, Fusio-technik® PP-RCT 125WOR resin meeting the short-term properties and   
long-term strength requirements of ASTM F 2389-17 and contain “White Oxidative Resistance”, (WOR). The pipe shall contain no rework or recycled materials and manufactured only from “virgin” resins. All pipes shall be made in a three-layer extrusion process. All pipes shall comply with the rated pressure requirements of ASTM F 2389-17. All pipe shall be certified as complying with NSF 14, NSF 61, NSF 51,   
ASTM F 2389-17 and CSA B137.11.

**2.02 Carrier Pipe Fittings:** Injection molded fittings shall be provided on all fittings through   
12” diameter unless otherwise approved as a “custom fitting” and manufactured from a   
high-quality Polypropylene Random Co-Polymer, PP-R Super 80 SDR5 resin meeting the   
short-term properties and long-term strength requirements of ASTM F 2389-17A. The fittings   
shall contain no rework or recycled materials and manufactured only from “virgin” resins.   
All fittings shall be certified by as complying with NSF 14, NSF 61, NSF 51 and ASTM F 2389   
or CSA B137.11. Fittings larger than 12” diameter shall be fabricated by Aquatechnik®   
North America using the same piping material furnished for the piping application and complying with NSF 14, NSF 61, NSF 51 and ASTM F 2389-17 or CSA B137.11.

**2.03 Carrier Pipe Insulation:** Carrier pipe insulation shall be HiTherm® PIR300 25/50   
polyisocyanurate foam injected with one shot into the annular space between carrier pipe and jacket. Insulation shall be rigid, >90% closed cell polyisocyanurate with a minimum 2.0 lbs per foot3 density, compressive strength of 30 psi @ 75˚F, an initial thermal conductivity K factor no higher than 0.14 @ 75˚F per ASTM C-518 and meet E84 25/50 flame/smoke passive fire resistance rating. Maximum continuous operating temperature of polyisocyanurate foam shall be -297˚F to 300˚F with infrequent allowances for intermittent spikes up to 350˚F.

**2.04 Insulation Fittings & Joints:** All straight joints and fitting joints shall be insulated using material supplied by system manufacturer.

**2.05 Outer Jacketing Fitting:** Provide metal covers designed to fit snugly on the jacketing to provide a watertight closure. All covers shall be banded in place with 3/8” wide aluminum or stainless steel straps and will be the same thickness as the jacketing.

**2.06 Jacketing Material:** Shall be spiral lock seam aluminum, galvanized steel or stainless steel in accordance with ASTM A366 and ASTM A256 G90 or as specified for above ground applications.

See **Table 1** for metal jacket thickness.

**Table 1:**

|  |  |  |
| --- | --- | --- |
| **Jacket Size**  **In Inches** | **Aluminum Jacket Spiral Seam with impact & chemical resistance equivalent to H-14 Temper T-3003 in accordance with ASTM-B 313.** | **Stainless & Galvanized Steel Jacket Spiral Seam in accordance  with ASTM A-366 ASTM A-26 G90.** |
| 4 | 22 Gauge | 26 Gauge |
| 6 | 22 Gauge | 26 Gauge |
| 8 | 22 Gauge | 26 Gauge |
| 10 | 22 Gauge | 26 Gauge |
| 12 | 22 Gauge | 26 Gauge |
| 14 | 18 Gauge | 22 Gauge |
| 16 | 18 Gauge | 22 Gauge |
| 18 | 18 Gauge | 22 Gauge |
| 20 & larger | 18 Gauge | 22 Gauge |

**2.07 Manufacturer’s Assistance:** Rovanco® will provide a field service man on-site to properly train the installing personnel in all phases of installation, (if required).

**2.08 Approved Vendor:** The Rovanco® Above Ground Pre-Insulated Foam Piping System is engineered with Fusio-technik® PP-RCT 125 carrier pipe. All other manufacturers wishing to bid on this project must be ISO 9001 certified and provide the engineer with certified test data from either foam manufacturer or an independent testing agency that the product is capable of withstanding the service temperature continuously. The manufacturer shall obtain written approval from the engineer 10 days prior to bid date. Contact our home office or local representative for insulation sizing.