20535 S.E. FRONTAGE ROAD

JOLIET, ILLINOIS 60431

PHONE: 815-741-6700

FAX: 815-741-9080

Email: chad@rovanco.com

Website: www.rovanco.com

ROVanCO

Piping Systems, Inc.

February 1, 2026

Part 1 – General

1.01	Stainless Steel by Stainless Steel Containment Piping

1.02	This system shall be a Below Ground Stainless Steel by Stainless Steel Containment Piping System with basis of design being Rovanco Piping Systems of Joliet, Illinois, Stainless Steel Double Wall Containment System.

Part 2 - Products

2.01	Carrier Pipe: Shall be schedule 10S type 2507 “Super” Duplex EFW Stainless Steel in accordance with ASTM A790 and supplied in 20’ lengths.

  - Inner Pipe Supports: All pipe shall be aligned and supported within the casing with like

material centering supports spaced on approximately 10’0”. The inner pipe shall bear directly on the support. The support shall be designed as to permit drainage and free air passage. Concrete type pipe supports will not be allowed.

2.03	Containment Casing: Shall be schedule 10S EFW type 304L Stainless Steel in accordance with ASTM A312 and supplied in 20’ lengths.

The exterior surface shall be smooth to permit free moisture drainage and removability of the inner assembly. The outer casing shall be sized to provide an adequate annular space between the outer surface of the pipe material and the interior surface of the casing.

Outer containment closures shall consist of like material and be field welded over adjacent units.  After tests all exposed closures shall be covered in the field with a polyurethane heat shrink material with a minimum thickness of 60 mils.

2.04	Weld Fittings: All changes in direction shall be made with bent or weld fittings of like material. Where tee branches are smaller than the mains they join, weld-o-lets may be used. All fittings shall be of like material the same wall thickness as adjacent piping. Fitting covers of like material and carrier fittings of like material will ship loose.

2.05	Anchors: Anchors shall be pre-fabricated onto the piping units and shall be equipped with drainage and vent openings at the top and bottom of the anchor plate. Anchor plates shall be made of ½” steel plate of like material.

2.06	End Seal: Terminal ends inside manholes, pits, or building walls shall be equipped with end seals consisting of a steel bulkhead plate welded to the pipe conduit. End seals shall be made of a ½” steel plate with drain or vent openings located diametrically opposite on the vertical center line of the mounting plate and shall be shipped to the jobsite with plugs in place.  Terminate containment 2 inches beyond the inside face of building walls to protect any exposed piping from damp wall condensation.

2.07	Field Tests: The inner pipe of the system shall be tested hydrostatically to 1-1/2 times the working pressure of the line.  If a leak is found, it shall be repaired and the test repeated.  The outer casing shall be tested with air at 15 psig and a soap solution shall be applied to the field joints to locate leaks.  If leaks occur, they shall be repaired and the test repeated.  After approved by test, all field joints shall be coated by the contractor.  Before backfilling, the contractor shall test the containment coating with an electric holiday detector.  Any breaks in the coating system will be repaired and the test repeated by the contractor.

2.08	Back Fill: Should be tampered compactly in place so as to assure a stable surface.  No rock shall be used in the first foot of backfill.  24 inches, top of pipe to grade, of compacted fill shall meet H-20 Highway loading.

2.09	Installation: The installation shall be made in accordance with plans and specifications, and manufacturers installation instructions.  Manufacturer will provide a field service instructor on-site prior to fabrication of the piping to confirm routing, anchoring, support, and termination details.  The field serviceman will also train the contractor in all phases of installation.

2.10	Approved Vendors: Stainless Steel Double Wall Containment System by Rovanco, Joliet, Illinois or approved equal. Any alternate supplier must be ISO 9001 Certified and submit their technical data to the engineer ten days prior to bid date to be approved in writing as an equal.